## Announcement: Differential pressure transmitter PS 17

Compact standard transmitter

- Either with one fixed measurement range or  toggling between 4 different measurement ranges (optional)

- Zero point correction and via internal pushbutton  or digital input

- Fine adjustment via internal pushbutton

- Can be calibrated

- Measuring symmetric and asymmetric measurement ranges

- Output signals can be configured using DIP switches

- Conversion into square root signal ad-justable

- Also as 2-wire system or with relay (optional)

- With LCD (optional)

- Top-hat rail mounting and wall surface installation IP 67

- Plug for easy commissioning (optional)

Technical data

Measurement

ranges:	50/100/200/500 Pa,
½.5/5/10/20/50/10 kPa (others on request)

Analog outputs: 	0..10 V, 2..10 V, 
0..20 mA, 4..20 mA

Power supply:	24 VAC/DC 
(50/60 Hz, ±10%)
15..32 VDC (two-wire)

24 VDC (with galvanic separation)

LCD: 	3 ½ digit (optional)

Contact points: 	1 switching relay
max. 230 VAC, 6 A (optional)

Margin of error: 	± 1 % of the set value (for measurement ranges ≤ 100 Pa  plus ± 0.5 Pa)

Temperature

coefficient span:	0.1 % of max. value / K

Temperature 
coefficient

zero point:	0.1 % of max. value / K

Max. system

pressure/Overload

capacity: 	± 25 kPa (measurement ranges ≤ 250 Pa)

± 50 kPa (measurement ranges > 250 Pa)

Medium: 	air, non-aggressive and non-flammable gases

Sensor response

time: 	25 ms

Time constant: 	25 ms .. 10 s adjustable

Ambient

temperature:

- 10 .. 70 ° C

with display: 0 .. 50 °

Storage

temperature: 	- 10 .. 70 ° C

with display: - 5 .. 55 ° C

Power

consumption: 	< 1 W 
(Option Relay: < 4 W)

Weight: 	approx. 200 g

Electrical

connection: 	spring-type terminal and cable glands 
2 x M 12 or 1 x M20 or M 12  plug (optional)

Pressure ports: 	for tubing 
NW 4 and 6 mm

Protection class: 	IP 67

Housing/ cover: 	ABS, top-hat rail assembly and wall mounting possible

Dimensions: 	103mm x 78mm x 65mm

Certificates: 	CE

Optional: 	DAkkS or ISO factory calibration certificate

Designation:	differential pressure transmitter

Type: 	PS 17

Manufacturer: 	halstrup-walcher GmbH